HPS Millennium™

1.2kV to 5kV Class General Purpose

Energy Efficient Dry-Type Medium Voltage

Distribution Transformer

Typical Specification

Canada

595 Southgate Drive

Guelph, Ontario

N1G 3W6

Phone: 1-888-798-8882

Fax: 1-519-822-9701

United States

1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

- GENERAL

  - SCOPE

    - This section defines dry-type, enclosed and ventilated energy efficient medium voltage transformer as indicated.

    - Transformers shall be designed, constructed and rated (where applicable) in accordance with U.S. Department of Energy, Energy Conservation Program for Commercial Equipment; Distribution Transformers Energy Conservation Standards (DOE 10 CFR Part 431) and/or the Canadian Energy Efficiency Regulations (SOR/94-651); for medium voltage, dry-type distribution transformers.

  - RELATED DOCUMENTS

    - Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section

  - REFERENCES

    - ANSI C57.12.01 Dry-Type Transformer For General Applications, CSA C9

    - IEEE C57.110

    - CSA C22.2 No. 47 and UL 1561

    - DOE 10 CFR Part 431 Efficiency Standards, Canadian Energy Efficiency Regulations SOR/94-651.

  - SUBMITALS

    - Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract.

      - Customer name. Customer location and customer order number shall identify all transmittals.

    - Product Data including kVA rating, temperature rise, detailed enclosure dimensions, primary & secondary nominal voltages, primary voltage taps, no load & full load losses per NEMA ST-20, impedances, unit weight, warranty, Efficiency (where applicable) per DOE 10 CFR Part 431 Efficiency Standards and/or the Canadian Energy Efficiency Regulations SOR/94-651; for medium voltage dry-type distribution transformers.

  - STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and if necessary, apply temporary heat where required to obtain suitable service conditions.

    - Handle transformer using proper equipment for lifting and handling, use when necessary lifting eye and/or brackets provided for that purpose.

  - WARRANTY

    - The transformer shall carry a 1 year limited warranty.

(For details, refer to the manufacturers published warranty)

- PRODUCTS

  - General construction:

    - Single phase and three phase medium voltage distribution transformers rated at 15kVA and larger, shall be ventilated type. All three phase transformers shall be constructed with three coils and a single core. The primary side of each transformer shall, if applicable, be provided with taps that meet or exceed NEMA standards. Convection air cooled.

    - Transformers shall be designed, constructed and rated in accordance with UL, CSA, and NEMA standards. If shipping to Europe, transformer will also have to be manufactured in accordance to CE standards and carry a CE mark.

    - If transformer is to be used for non-linear load applications, the transformer shall be de-rated as per ANSI/IEEE C57.110.

  - Voltage and kVA Requirements:

    - Primary Voltage:   Single Phase - [2400][4160][other] Volts

Three Phase - [2400][4160][other] Volts

    - Primary Voltage BIL Rating: [20][30][45][60] other

    - Secondary Voltage: Single Phase - [120/240][other] Volts

Three Phase - [208Y/120][480Y/277][600Y/347][other] Volts

    - Secondary Voltage BIL Rating: [10][20][30] other

    - kVA Rating:  Single Phase - [15][25][37.5][50][75][100][150][167][250][333][other]

Three Phase - [15][30][45][75][112.5][150][225][300][500][750][1000][1500][other]

    - System Frequency:  60 Hertz

  - Basic Requirements:

    - Standard impedance at 60Hz: Typically 4% to 6.5%

    - Nameplate Rating:  Linear load, 60Hz

    - Insulation Class:  220°C system [200][other]

    - Temperature Rise:  150°C [130°C][115°C][80°C][other]

    - Efficiencies: (where applicable)

      - Meets or exceeds DOE 10 CFR Part 431 Efficiency Standards and/or Canadian Energy Efficiency Regulations SOR/94-651 efficiencies at 50% of rated load.

      - Efficiencies are calculated under a linear load profile.

      - Efficiencies and load losses will be calculated at temperature reference of 75°C at Unity Power Factor (UPF).

      - Refer to the DOE 10 CFR Part 431 Efficiency Standards and Canadian Energy Efficiency Regulations SOR/94-651 for product exemption criteria

    - Taps: [2 x 2.5% FCAN and 2 x 2.5% FCBN)][none][other]

    - Core construction: high grade non-aging, fully processed silicon steel laminations or better.

    - Coil conductors: aluminum [copper] windings, with terminations brazed, welded or bolted.

    - Impregnation: vacuum impregnated core & coils.

    - Sound: as per ANSI C57.12.01.

    - Enclosure:  ventilated, NEMA 3R [NEMA 3R c/w filters][other].

    - Enclosure Finish:  ANSI 61 Grey suitable for UL50 outdoor applications [other].

    - Transformers shall terminate in mounting pads. Lugs will be included on all aluminum and copper units up to and including 270 amp ratings. Contractors shall provide all necessary lugs not already provided with transformer.

    - Anti-vibration pads/isolators shall be used between the transformer core and coil and the enclosure.

    - Ground Pads: standard

    - UL listed, CSA approved, [CE Mark].

    - Built in accordance with all applicable UL, CSA and ANSI/IEEE standards.

    - Ground core & coil assembly to enclosure with a flexible copper grounding strap or equivalent.

    - Seismic:  Meets all seismic parameters for IBC 2009 and NBCC 2005 for ground level installations only for all locations in North America.

    - Mounting:

      - Ventilated units up to 750 lbs.: Suitable for wall, floor or ceiling mounting (drip plate required).

      - Ventilated units over 750 lbs.: Suitable for floor mounting only.

Options:

- Electrostatic shielding

- Vibration Isolators

- Low Sound: [-3 dB][-5 dB][-8 dB]

- Enclosures: [Type 4][Type 4X][Type 12] other

- Over-Temperature switches wired to internal terminal strip. Temperatures specified for use with class 220°C insulation systems. Standard configuration is N.C. opening on high temperature. Optional configuration is N.O. closing on high temperature. Installation options: [one switch: 170°C or 200°C on center coil][two switches: 170°C and 200°C on center coil][six switches: one 170°C and one 200°C on each of the 3 coils]

- Strip Heaters

- Fans

- SPD (Surge Protection Device)

- Manufacturer has the ability to guarantee EMF levels as low as 10mG on the enclosure top and four sides from a distance of 1 meter for most units and kVA ranges. (Contact manufacturer for details on pricing and availability.)

  - Acceptable Product and Manufacturer:

    - HPS Millennium™ transformer, by: Hammond Power Solutions Inc. (Canada: 1-888-798-8882 / U.S.: 1-866-705-4684).

    - Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.

##### EXECUTION

  - Installation

    - The installing contractor shall install the HPS Millennium™ Energy Efficient Medium Voltage Distribution Transformer per the manufacturer's recommended installation practices as found in the installation, operation, and maintenance manual and comply with all applicable codes.

    - Make sure that the transformer is level.

    - Check for damage and loose connections.

    - Mount transformer to comply with all applicable codes.

    - Install optional vibration isolation pads between transformer enclosure and the mounting surface.

    - Install seismic restraint where indicated on the drawing.

    - Coordinate all work in this section with all work of other sections.

    - Prior to energizing transformer, verify secondary voltages and if necessary adjust primary taps.